## 1.0	Purpose and Scope

The purpose of this document is to provide requirements and guidance for the application of the risk-based approaches to managing the lifecycle of safety instrumented systems (SIS) as specified in the IEC/ISA 61511 standard.  While the standard limits its scope to consequences related to safety and the environment, the same techniques can be used to address financial losses such as equipment damage and business interruption.

This standard is applicable when instrumentation, electrical, or electronic equipment is used as a part of an instrumented system that needs to be able to function upon demand to reduce risk to a tolerable level.  The types of risks that are in the scope of this standard are those where the consequences of failure include:

- Process safety risk

- Environmental risk

- Commercial risks can be considered using the same techniques described in this standard but are not required to be addressed using these techniques.

This standard specifies the management activities that need to be applied to all stages of the development and use of such systems.  It includes requirements for planning, competency, verification, and functional safety assessment.  This standard is only concerned with the functional safety provided by safety instrumented systems, although, consideration is given to other means of risk reduction when developing the requirements for such systems.

## 2.0	Normative References

The following normative documents contain requirements that, through reference in this text, constitute requirements of this technical practice.  For dated references, subsequent to amendments to, or revisions of, any of these publications do not apply.  However, parties to agreements based on this technical practice are encouraged to investigate the possibility of applying the most recent editions of the normative documents indicated below.  For undated references, the latest edition of the normative document referred to applies.

- IEC 61511-1-2016, Functional safety – Safety instrumented systems for the process industry sector – Part 1: Framework, definitions, system, hardware and application programming requirements

## 3.0	Terms, Definitions, Symbols, and Abbreviations

For the purposes of this standard, the terms and definitions given in IEC 61511-1-2016 shall apply.

The following abbreviations are used in this standard.

ALARP		As Low As Reasonably Practicable

IEC		International Electrotechnical Commission

IPF		Instrumented Protective Function

IPL		Independent Protection Layers

ISA		International Society of Automation

ISO		International Organisation for Standardisation

LOPA		Layer of Protection Analysis

PHA		Process Hazards Analysis

SIF		Safety Instrumented Functions

SIS		Safety instrumented system

## 4.0	Organization and Resources

Functional safety activities in this organization are defined in this standard at the physical site level.  The following table includes a step-by-step workflow of the activities that are associated with functional safety.  For each step, the personnel who are required to perform activities for that step are listed by role.  The table below is consistent with the format shown in Table 2 – SIS Safety Lifecycle Overview, as contained in the IEC 61511-1 standard.  It should be noted that while the first 8 tasks are chronological, on a project-by-project bases, tasks 9 though 11 are management and administration tasks that must be in place prior to executing the earlier tasks in the table.  It is the responsibility of the Engineering Manager to ensure that all of the tasks shown in Table 1 below are assigned to appropriate personnel and that they are aware of their responsibilities and are competent to perform those responsibilities.

Table 1 – Organization and Resources for Functional Safety Management

| Safety lifecycle phase | Task | Roles Responsible | Outputs generated | Tools/Resources |
| --- | --- | --- | --- | --- |
| 1. Hazard and Risk analysis | Schedule hazard and risk analysis for all existing equipment, new projects, all relevant modifications, and revalidations | PSM Coordinator | PHA Schedule, including resources | Personnel Schedule (MS Outlook), Conference Room, Web Conference (MS Teams) |
|  | Facilitate and document the hazard and risk analysis | PSM Coordinator | Hazard and risk analysis report, including worksheets, resulting lists of IPLs to be managed, and recommendations | Kenexis Open PHA Software, Layer of Protection Analysis – SIL Selection Procedure |
|  | Develop list of instrumented IPLs, including SIFs require to be included in scope of hazard and risk analysis | SIS Engineer | Expected IPL list | Kenexis Vertigo Software |
|  | Participate in the hazard and risk analysis | Process Engineer | Meeting discussion input | N/A |
|  |  | SIS Engineer | Meeting discussion input | N/A |
|  |  | Operations Representative | Meeting discussion input | N/A |
| 2. Allocation of safety functions to protection layers | Manage implementation of recommendations generated from hazard and risk assessment | PSM Coordinator | Recommendation assignment and close out | Kenexis Open PHA Software, Kenexis Integrated Safety Suite Recommendation / Action Item Dashboards |
|  | Submit IPL lists to engineering disciplines for implementation and management | PSM Coordinator | IPL lists by engineering discipline | Kenexis Open PHA Software |
| 3. SIS safety requirements specifications | Develop and document Safety Requirements Specifications (SRS) | SIS Engineer | Conceptual design of all SIF, including inputs, outputs, and logic solvers and selected equipment | Kenexis Vertigo Software |
| 4. SIS design and engineering | Define safety instrumented functions | SIS Engineer | SIF (IPF) List | Kenexis Vertigo Software |
|  | Perform conceptual design of all SIF | SIS Engineer | Conceptual design of all SIF, including inputs, outputs, and logic solvers and selected equipment | Kenexis Vertigo Software, Qualified Vendors Lists |

Table 1(cont’d) – Organization and Resources for Functional Safety Management

| Safety lifecycle phase | Task | Roles Responsible | Outputs generated | Tools/Resources |
| --- | --- | --- | --- | --- |
| 4. SIS design and engineering (continued) | Perform SIL verification calculations and modify equipment design as required to achieve selected performance targets | SIS Engineer | SIL verification calculations and report | Kenexis Vertigo Software |
|  | Manage implementation of recommendations generated from hazard and risk assessment | SIS Engineer | Safety Requirements Specifications Documentation and/or Report | Kenexis Vertigo Software |
|  | Perform SIL verification calculations and modify equipment design as required to achieve selected performance targets | SIS Engineer | SIL verification calculations and report | Kenexis Vertigo Software, Kenexis Arbor Software |
|  | Specify, requisition, purchase, and configure SIS equipment | SIS Engineer | Requisitions, configurations | N/A |
|  | Program SIS equipment and logic solvers | SIS Engineer | SIS programs | Vendor SIS maintenance and engineering interface |
|  | SIS detailed design drawings for installation and constructions | Instrumentation and control construction contractor or equipment vendor | Loop diagrams, wiring diagrams, panel layout diagrams, termination drawings, location plans | N/A |
| 5. SIS installation, commissioning, and validation | Install SIS equipment | Instrumentation and control construction contractor or equipment vendor | Installed SIS equipment | N/A |
|  | Commission SIS instruments, including installation validation | SIS Technician | Completed Loop Check Folders, Punchlist items as required | Kenexis OpScope – Field Loop Check Procedure Sheets, Kenexis Vertigo |
|  | Manage resolution of commissioning punch list items | SIS Engineer | Punch list item resolution and close out | Kenexis OpScope, Kenexis Integrated Safety Suite Dashboards |
|  | Perform factory acceptance test of SIS | SIS Technician |  | Kenexis OpScope – FAT Procedure |
|  | Manage resolution of commissioning punch list items | SIS Engineer | Completed FAT report, punch list items as required | Kenexis OpScope, Kenexis Integrated Safety Suite Dashboards |

Table 1(cont’d) – Organization and Resources for Functional Safety Management

| Safety lifecycle phase | Task | Roles Responsible | Outputs generated | Tools/Resources |
| --- | --- | --- | --- | --- |
| 5. SIS installation, commissioning, and validation (continued) | Perform site acceptance test of SIS (inclusive of field instruments) | SIS Technician |  | Kenexis OpScope – SAT Procedure |
|  | Manage resolution of commissioning punch list items | SIS Engineer | Completed SAT report, punch list items as required | Kenexis OpScope, Kenexis Integrated Safety Suite Dashboards |
| 6. SIS operation and maintenance | Develop test plans for all SIS equipment for all test types of that equipment | SIS Engineer | SIS Test Plans | Kenexis OpScope |
|  | Develop procedures for operations staff interaction with SIS | SIS Engineer | Operating procedures for interaction with the SIS | Kenexis OpScope |
|  | Include all SIS equipment in a maintenance management system for scheduling and tracking of periodic function tests | SIS Engineer | SIS Equipment Testing List | Kenexis Vertigo, Work Scheduling System |
|  | Schedule testing of SIS equipment in accordance with SRS | Maintenance Planner | Work schedules for SIS testing | Kenexis Vertigo, Work Scheduling System |
|  | Perform periodic function tests of SIS equipment | SIS Technician | SIS equipment test performance and results records | Kenexis Vertigo, Kenexis OpScope |
|  | Perform repairs or replacement of SIS equipment | SIS Technician | SIS equipment re-test results records | Kenexis Vertigo, Kenexis OpScope |
| 7. SIS modification | Review all modification requests to ensure that they are appropriately included in the management of change system and ensure that changes that may impact SIS are reviewed by an SIS Engineer | PSM Coordinator | Reviewed management of change items | Management of change database |
|  | Review all management of change items related to SIS as assigned by the PSM coordinator. If applicable, begin a project including all relevant SIS safety lifecycle steps to address the change. | SIS Engineer | Reviewed management of change items, initiation of new related SIS projects | Management of change database, Kenexis Vertigo |

Table 1(cont’d) – Organization and Resources for Functional Safety Management

| Safety lifecycle phase | Task | Roles Responsible | Outputs generated | Tools/Resources |
| --- | --- | --- | --- | --- |
| 8. De- commissioning | Review all decommissioning requests to ensure that they are appropriately included in the management of change system and ensure that decommissioning that may impact SIS are reviewed by an SIS Engineer | PSM Coordinator | Reviewed management of change items | Management of change database |
|  | Review all decommissioning management of change items related to SIS as assigned by the PSM coordinator. If applicable, begin a project including all relevant SIS safety lifecycle steps to address the change, especially where equipment4 that will remain in service will be impacted | SIS Engineer | Reviewed management of change items for decommissioning, initiation of new related SIS projects | Management of change database, Kenexis Vertigo |
| 9. SIS Verification | Perform a verification review of all work products / deliverables generated during tasks 1-8 to identify any problems | SIS Engineer or Engineering Manager | Review of work product related recommendations | Kenexis Vertigo, Kenexis Open PHA |
|  | Manage resolution of recommendations generated during verification activities | SIS Engineer or Engineering Manager | Recommendation assignment and close out | Kenexis Vertigo, Kenexis Open PHA, Kenexis Integrated Safety Suite Dashboards |
| 10. SIS functional safety assessment | Schedule a functional safety assessment for all completed SIS projects | Engineering Manager | Functional safety assessment schedule, including resources | Personnel Schedule (MS Outlook), Conference Room, Web Conference (MS Teams) |
|  | Perform a functional safety assessment for all completed | SIS Engineer (not involved in project execution) | Functional safety assessment report including recommendations to close out findings and gaps | Kenexis Open Audit software |
|  | Manage resolution of recommendations generated during functional safety assessment activities | Engineering Manager | Recommendation assignment and close out | Kenexis Open Audit software, Kenexis Integrated Safety Suite Dashboards |

Table 1(cont’d) – Organization and Resources for Functional Safety Management

| Safety lifecycle phase | Task | Roles Responsible | Outputs generated | Tools/Resources |
| --- | --- | --- | --- | --- |
| 10. SIS functional safety assessment (continued) | Schedule a safety instrumented systems audit during the same time frame as the process safety management audit | Engineering Manager | Functional safety audit schedule, including resources | Personnel Schedule (MS Outlook), Conference Room, Web Conference (MS Teams) |
|  | Perform a functional safety audit | SIS Engineer (not involved in project execution) | Functional safety audit report including recommendations to close out findings and gaps | Kenexis Open Audit software |
|  | Manage resolution of recommendations generated during functional safety audit activities | Engineering Manager | Recommendation assignment and close out | Kenexis Open Audit software, Kenexis Integrated Safety Suite Dashboards |
| 11. Safety lifecycle structure and planning | Develop and maintain an SIS safety lifecycle management plan | Engineering Manager | SIS safety lifecycle management procedure (this document) | SIS safety lifecycle management procedure (this document) |
|  | Assign task responsibilities to specific personnel related to SIS safety lifecycle management activities | Engineering Manager | Personnel role descriptions, Personnel role and task assignment documentation | Human resource management software |
|  | Ensure competency of personnel assigned SIS safety lifecycle management | Engineering Manager | Training documentation, comprehension assessment documentation, verification of suitable work production documentation | Kenexis learning management system and training courses |
|  | Periodically review the work activities of all staff assigned SIS safety | Engineering Manager | Personnel performance review documentation | Human resource management software |

The tasks described in Table 1 included a number of roles that are required to achieve functional safety.  A single role might be assigned to multiple different staff members, depending on the volume of work required to be performed and duration of activities being performed (e.g., the same role might need to be filled in multiple different shifts).  Similarly, multiple different roles might be filled by a single individual, especially in smaller organizations.  The roles shown below are effective in this organization, and the person or persons assigned to those roles are defined in human resources management documentation. These roles are further described in the table below.

Table 3 – Roles and Responsibilities Related to Functional Safety

| Role | Reports to | Responsibilities |
| --- | --- | --- |
| Engineering Manager | Plant Manager | The Engineering Manager is primarily responsible for creating a plan to achieve functional safety, maintaining that plan, and verifying and auditing activities to ensure that the plan is being implemented. The Engineering Manager is also responsible for ensuring the resources are available to execute the plan, and that human resources executing the plan are informed of their responsibilities and competent to execute them. |
| PSM Coordinator | Engineering Manager | The PSM Coordinator is responsible for ensuring that hazard and risk analysis activities associated with are scheduled, executed, and appropriately staffed. This activity also includes tracking the resolution of recommendations that result from these activities to conclusion. The PSM coordinator is also responsible for the Management of Change process. |
| SIS Engineer | Engineering Manager | The SIS Engineer is responsible for design and calculation activities that are associated with the SIS safety lifecycle. This includes participation in hazard and risk analysis, conceptual design and SIL verification, safety requirements specifications, test procedure development, and validation. |
| SIS Technician | Maintenance Manager | The SIS Technician is primarily responsible for maintenance activities on SIS equipment, including testing, corrective maintenance, and preventive maintenance. The SIS Technician is also responsible for ensuring the that results of testing and maintenance activities are appropriately recorded. |
| Maintenance Planner | Maintenance Manager | The Maintenance Planner ensures that resources are available and assigned to perform SIS testing and maintenance activities. |
| Maintenance Manager | Plant Manager | The Maintenance Manager is responsible for ensuring that resources are available to execute SIS maintenance and testing activities, including resources for scheduling and tracking. |

The SIS Safety Lifecycle, in addition to human resources, also requires administrative tools and software applications to ensure that all steps of the safety lifecycle are appropriately implemented and that all ongoing activities are appropriately scheduled and completed.  These tools also help to ensure follow up on any recommendations are deviations that are noted during the SIS Safety Lifecycle.

Table 4 – Tools/Resources Utilized for Functional Safety

| Tool | Description |
| --- | --- |
| Personnel Scheduling Tool | The personnel scheduling tool is utilized to assign work activities, durations, and locations related to SIS Safety Lifecycle activities, and also to allow for communications about these activities. |
| Kenexis Open PHA | Kenexis Open PHA is a facilitation and documentation tool that is utilized to record the discussions, results, and recommendations from hazard and risk analysis studies. This includes: - PHA (HAZOP) documentation - LOPA documentation - HAZOP / LOPA recommendation tracking |
| Kenexis Vertigo | Kenexis Vertigo is an SIS Safety Lifecycle Management tool that is utilized to design and document SIS equipment. This includes: - SIF list development - Non-SIS IPF lists - SIL verification calculations - Safety requirements specifications - SIS/IPL recommendation tracking |
| Kenexis Arbor | Kenexis Arbor is a fault tree analysis tool that is utilized to perform complex frequency and availability calculations. This includes: - SIL verification for special or complex systems - Hazard and risk analysis for special or complex systems |
| Kenexis OpScope | Kenexis OpScope is a procedure development, execution, and tracking tool that allows procedures to be written, and then allows tracking and performance of those procedures through a hand-held device. For the SIS Safety Lifecycle this includes: - Development of SIS equipment testing procedures - Performance and tracking of loop checks - Performance and tracking of factory acceptance testing (FAT) - Performance and tracking of site acceptance testing (SAT) - Performance and tracking of periodic SIS Testing |
| Kenexis Open Audit | Kenexis Open Audit is an audit protocol development, and audit/assessment facilitation, documentation, and tracking tool. This includes: - SIS audit protocol development - SIS functional safety assessment protocol development - SIS audit facilitation and documentation - SIS functional safety assessment facilitation and documentation - SIS audit finding and recommendation tracking - SIS functional safety assessment finding and recommendation tracking |
| Management of Change Database | The management of change database is a tool that is utilized to review, assess, document, and approve all significant changes to process equipment. |

Use of External Organizational Resources

While the organization is responsible for the overall results and activities of the SIS Safety Lifecycle, in some cases it is not the best choice to have all SIS Safety Lifecycle Activities performed by internal organization personnel.  In these cases, using contract resources to perform the activities is optimal.  IEC 61511 allows for the use of external contract resources to execute SIS Safety Lifecycle activities, but those resources must be managed appropriately.  Specifically, the external resource must deliver products and services as specified by our organization and do so in accordance with a quality management system.  Our organization requires this to be proven through third party certification to the ISO 9001 standard for all relevant services and products.  These external providers shall also have, and submit for review, a functional safety management system plan and have procedures in place to demonstrate the adequacy of the functional safety management system.  Once these documents are submitted and approved by the engineering manager, those external resources are listed in Table 4, below.

Table 4 – Qualified External Organizational Resources for Functional Safety

| Task | Qualified External Organization |
| --- | --- |
| Hazard and Risk Analysis Facilitation | Kenexis |
| SIF List / IPL List Development | Kenexis |
| Safety Requirements Specifications Development | Kenexis |
| SIL Verification Calculations | Kenexis |
| SIS Equipment Requisition/Purchase | (QUALIFIED EXTERNAL ENGINEERING COMPANY) |
| SIS Installation | (QUALIFIED EXTERNAL ENGINEERING COMPANY) |
| SIS Equipment Commissioning | (QUALIFIED EXTERNAL ENGINEERING COMPANY) |
| FAT Procedure Development/Facilitation | Kenexis |
| SAT Procedure Development/Facilitation | Kenexis |
| SIS Test Plan Development | Kenexis |
| SIS Test Performance | (QUALIFIED EXTERNAL SERVICE COMPANY) |
| SIS Functional Safety Assessment | Kenexis |
| SIS Audit | Kenexis |

## 5.0	Competency

Section 4.0 of this document laid out the organizational structure and resources that are required to execute SIS Safety Lifecycle activities, including the definitions of tasks and assignment of responsibilities to roles.  In order to perform these activities, personnel assigned to the roles must be competent to execute the activities.  Determination of the competency of any individual to perform SIS Safety Lifecycle activities is performed by the persons who have assigned those responsibilities as defined in Table 3.  In order to ensure competency, the resource must be trained and qualified to perform those activities.  Training can occur through any combination of external or internal lectures, demonstrations, and exercise activities.  Qualification requires that a competent person in an activity observes a candidate performing the activity and reviews the results to ensure that the activity is performed correctly.  Competency requirements for all SIS Safety Lifecycle Management activities are shown in Table 5, below.  The results of training and competency assessment shall be documented in the site learning management system software database.

Table 5 – Competency Requirements Related to Functional Safety

| Role | Activity/Competence Requirement | Competency/Training Requirement |
| --- | --- | --- |
| Engineering Manager | General Process Safety Management – Overview and Regulations | Kenexis Training – OSHA Process Safety Management and EPA RMP Overview |
|  | SIS Safety Lifecycle Overview | Kenexis Training – Safety Instrumented Systems – Overview and Awareness |
|  | SIS Implementation Management Activities | Kenexis Training – Safety Instrumented Systems Management Responsibilities |
| PSM Coordinator | General Process Safety Management – Overview and Regulations | Kenexis Training – OSHA Process Safety Management and EPA RMP Overview |
|  | SIS Safety Lifecycle Overview | Kenexis Training – Safety Instrumented Systems – Overview and Awareness |
|  | Facilitate and Document Hazard and Risk Analysis Studies | Kenexis Training – Unified Hazard Assessment Facilitation and Documentation – Process Hazards Analysis, Layer of Protection Analysis, and Bowtie Diagram Analysis |
|  | Using PHA Software | Kenexis Training – Using Open PHA |
|  | Using Audit Software | Kenexis Training – Using Open Audit |
| SIS Engineer | General Process Safety Management – Overview and Regulations | Kenexis Training – OSHA Process Safety Management and EPA RMP Overview |
|  | SIS Safety Lifecycle Overview | Kenexis Training – Safety Instrumented Systems – Overview and Awareness |
|  | Facilitate and Document Hazard and Risk Analysis Studies | Kenexis Training – Unified Hazard Assessment Facilitation and Documentation – Process Hazards Analysis, Layer of Protection Analysis, and Bowtie Diagram Analysis |
|  | Using PHA Software | Kenexis Training – Using Open PHA |
|  | SIL Verification Calculations | Kenexis Training – Safety Integrity Level Verification |
|  | Using SIL Verification Software | Kenexis Training – Using Vertigo |
|  | Safety Requirements Specifications | Kenexis Training – Safety Requirements Specifications |

Table 5 (Cont’d) – Competency Requirements Related to Functional Safety

| Role | Activity/Competence Requirement | Competency/Training Requirement |
| --- | --- | --- |
| SIS Engineer (cont’d) | Safety Requirements Specifications | Kenexis Training – Safety Requirements Specifications |
|  | SIS Certification | ISA Training – ISA EC50/52/54 and certification exam for ISA 84 Expert certification |
|  | Using Fault Tree Software | Kenexis Training – Using Arbor |
|  | Using SIS Testing Management Software | Kenexis Training – Using OpScope |
| SIS Technician | General Process Safety Management – Overview and Regulations | Kenexis Training – OSHA Process Safety Management and EPA RMP Overview |
|  | SIS Safety Lifecycle Overview | Kenexis Training – Safety Instrumented Systems – Overview and Awareness |
|  | SIS Maintenance Requirements Overview | Kenexis Training – Safety Instrumented Systems – Maintenance Responsibilities |
|  | Participating in Hazard and Risk Analysis Studies | Kenexis Training – Layer of Protection Analysis Participant Training |
|  | Calibrating and Testing SIS Equipment | ISA Training – ISA Technician Bootcamp |
|  | Technician Certification | ISA Certification – Certified Control Systems Technician |
|  | Using SIS Testing Management Software | Kenexis Training – Using OpScope |
| Operations Representative | General Process Safety Management – Overview and Regulations | Kenexis Training – OSHA Process Safety Management and EPA RMP Overview |
|  | SIS Safety Lifecycle Overview | Kenexis Training – Safety Instrumented Systems – Overview and Awareness |
|  | SIS Operations Requirements Overview | Kenexis Training – Safety Instrumented Systems – Operations Responsibilities |
|  | Participating in Hazard and Risk Analysis Studies | Kenexis Training – Layer of Protection Analysis Participant Training |
| Maintenance Planner | General Process Safety Management – Overview and Regulations | Kenexis Training – OSHA Process Safety Management and EPA RMP Overview |
|  | SIS Safety Lifecycle Overview | Kenexis Training – Safety Instrumented Systems – Overview and Awareness |
|  | SIS Maintenance Requirements Overview | Kenexis Training – Safety Instrumented Systems – Maintenance Responsibilities |

Table 5 (Cont’d) – Competency Requirements Related to Functional Safety

| Role | Activity/Competence Requirement | Competency/Training Requirement |
| --- | --- | --- |
| Maintenance Planner | General Process Safety Management – Overview and Regulations | Kenexis Training – OSHA Process Safety Management and EPA RMP Overview |
|  | SIS Safety Lifecycle Overview | Kenexis Training – Safety Instrumented Systems – Overview and Awareness |
|  | SIS Maintenance Requirements Overview | Kenexis Training – Safety Instrumented Systems – Maintenance Responsibilities |
|  | SIS Implementation Management Activities | Kenexis Training – Safety Instrumented Systems Management Responsibilities |

## 6.0	Information and Documentation Requirements

Implementation of the SIS Safety Lifecycle results in the generation of documentation of the SIS and related activities.  This documentation is required to be available to personnel involved in any SIS Safety Lifecycle activities.  In order to ensure that the documentation is always up to date, the official repository for SIS information is the study documented contained in the Kenexis Integrated Safety Suite (KISS), including Kenexis Open PHA studies for Hazard and Risk Analysis and Kenexis Vertigo Studies for SIS Safety Lifecycle Management.  As required, reports can be generated using the KISS software, but these reports are not the official record and shall not be used for activities beyond those for which they were immediately printed.